## Completion Data Checklist
Completion data checklist
LV Networks | Sent | LV Substation Information | Sent | HV + Substation Inforation | Sent | Water Networks | Sent
Mains Job Card |  | Transformer Factory Test Certificate |  | RMU Commissioning Certificate |  | Completed Work Form
Service Card |  | LV Cabinet Commissioning Certificate |  | HV Metering CT & VT Certificates |  | Pressure Test Certificates
CT/VT Certificate (If above 69kvA) |  | CT/VT Certificates (if ACB installed) |  | Substation Earthing Resistance Certificate |  | Sample Test Certificates
As-laid (PDF, CAD, Visio etc.) |  | Small Power and Lighting Testing |  | Final As-laid (PDF, CAD, Visio etc.) |  | Completed Vesting Certificate
BNO Details (If applicable) |  | As-laid (PDF, CAD, Visio etc.) |  | HV As-laid Drawing (PDF, CAD, Visio etc.)
HV Cable Test Certificates
Small Power and Lighting Testing
LP Networks | Sent | MP Networks | Sent | Manifolds | Sent | PRI Information | Sent
CSEP MTC |  | CSEP MTC |  | CSEP MTC |  | Factory test, technical data sheet, make, model, serial number
Mains Test Certificates for connect plots |  | Mains Test Certificate |  | Mains Test Certificate PE |  | Commissioning Details, Settings, Pressure Level
Service Card(s) |  | Service Card(s) |  | Mains Test Certificate Steel |  | As-laid (PDF, CAD, Visio etc.)
Meter Card(s) |  | Meter Card(s) |  | Certificate of Compliance |  | MP Pipe as Laid Drawing, PDF, CAD, Visio, Any Scaled format drawing
Final As-laid (PDF, CAD, Visio etc.) |  | Valve record card of PIV installed |  | Post Construction Audit
|  | Photograph of MP Meter |  | Valve sketch and valve record card, complete with make, model and serial no.
|  | Final As-laid (PDF, CAD, Visio etc.) |  | Certificate of conformity (if a prefabricated unit has been purchased)
Welder’s qualifications and welding inspection report (If Applicable)
Final As-laid (PDF, CAD, Visio etc.)
Photographs
Ventilation provision
A3 composite and meter tie on labels.
That the Gas supply entry into the property has been sealed internally and externally.
That each meter is labelled with the property number it serves
That an IIV has been installed.
Meter Manifold itself, with meters installed.
SIV covers
Of a sign positioned on the outside of the meter enclosure/compartment that advises where the key to the meter enclosure/compartment may be found.

## LP Gas Networks
Low Pressure Networks Completion Data Requirements
Mains Test Certificate
Length of mains laid and tested
Please separate the length by each mains size e.g. 10m x 63mm, 10m x 90mm etc.
Please include node or plot numbers
Test Results
Test start and end date + time
Test start and end pressures
Engineers signature
Signed Date
Service Card
Mains Size
Engineers Signature
Signed Date
Test Results
Test Pressure & Time
Meter Cards
MPRN
Meter Serial Number
Plot Number
Meter Reading
Engineers Signature
Date Fitted
Final As-laid
Mains size
CSEP coordinates
Depth of CSEP and all mains
Locational Dimensions along all ESP mains
Please include 2 dimensions for the CSEP and each cap end
Service Route for services that do not follow a perpendicular route. i.e. straight route from mains to meter

## MP Gas Networks
Medium Pressure Networks Completion Data Requirements
Mains Test Certificate
Length of mains laid and tested
Please separate the length by each mains size e.g. 10m x 63mm, 10m x 90mm etc. Please include node or plot numbers
Test Results
Test start and end date + time Test start and end pressures
Engineers signature
Signed Date
Service Card
Mains Size
Engineers Signature
Signed Date
Test Results
Test Pressure & Time
Meter Cards
MPRN
Meter Serial Number
Plot Number
Meter Reading
Engineers Signature
Date Fitted
Valve Record Card
Valve Sketch
Valve Make, Model & Serial Number
Governor Test Certificate
Photographs
MP Meter, showing distance from window/door
Termination of the vent tip
Final As-laid
Mains size
CSEP coordinates
Depth of CSEP and all mains
Locational Dimensions along all ESP mains
Please include 2 dimensions for the CSEP and each cap end
Service Route for services that do not follow a perpendicular route. i.e. straight route from mains to meter

## Manifold
Manifold Completion Data Requirements
Mains Test Certificate
Length of mains laid and tested
Please separate the length by each mains size e.g. 10m x 63mm, 10m x 90mm etc.
Please include node or plot numbers
Test Results
Test start and end date + time
Test start and end pressures
Engineers signature
Signed Date
Steel Test Certificate
Steel Size
Engineers Signature
Signed Date
Test Results
Test Pressure & Time
Manifold Information
Certificate of Compliance
Post Construction Audit
Valve sketch and valve record card, complete with make, model and serial no.
Certificate of conformity (if a prefabricated unit has been purchased)
If welded, welder’s qualifications and welding inspection report
Photographs
Ventilation provision
A3 composite and meter tie on labels.
That the Gas supply entry into the property has been sealed internally and externally.
That each meter is labelled with the property number it serves
That an IIV has been installed.
Meter Manifold itself, with meters installed.
SIV covers
Of a sign positioned on the outside of the meter enclosure/compartment that advises where the key to the meter enclosure/compartment may be found.
Final As-laid
Mains size
CSEP coordinates
Depth of CSEP and all mains
Locational Dimensions along all ESP mains
Please include 2 dimensions for the CSEP and each cap end
Service Route for services that do not follow a perpendicular route. i.e. straight route from mains to meter

## PRI Information
PRI Completion Documents
Mains Test Certificate
Medium Pressure MTC Please see MTC checklist
Low Pressure MTC Please see MTC checklist
PRI Test Certificate (Provided by the manufacturer)
Valve Record Card
Valve Sketch
Valve Make, Model & Serial Number
Function of Valve

## LV Electric Networks
LV Electric Completion Data Requirements
Mains Job Card
LV cable testing
Commissioning and Energisation Results
Mains Cable Type
Size
Destination
Service Card
Service Cable Size
Mains Cable Size
Cut Out Rating
Fuse Size
Phase Number
ELI Readings (Reading needs to be under 0.35)
Voltage readings (between 216-253)
Phase Rotation
Sketch/Drawing As-laid
Install Date
Engineers Signature
Metering CT/VT Commissioning Certificate (If larger than a 69kVA supply)
Inuslation Resistance
Polarity Checks
Injection Testing
CT Class
Burden
Ratio
As-laid (PDF, CAD, Visio, Any Scaled Format)
Main outside plot is connected to linkbox/transformer
Service Route if not on the Service Card
Locational dimensions on live cables and linkbox
BNO (If applicable)
BNO details - contact number, address etc.

## LV Substation
LV Electric Completion Data Requirements
Transformer Factory Routine Test Certificate
Manafacturers Standard Test Certificate
LV Cabinet Commissioning Certificate
Insulation Resistance
Fuse Rating
Circuit Name
Voltage
ELI
Phase Rotation
Protection Settings (for ACB's)
Metering CT/VT Commissioning Certificate (If ACB installed)
Inuslation Resistance
Polarity Checks
Injection Testing
CT Class
Burden
Ratio
Small Power and Lighting Testing
Voltage
ELI
Circuit Rating
As-laid (PDF, CAD, Visio, Any Scaled Format)
Main outside plot is connected to linkbox/transformer
Service Route if not on the Service Card
Locational dimensions on live cables and linkbox

## HV + Substation
HV + Substation Electric Completion Data Requirements
RMU Commissioning Certificate
Continuity
Insulation Resistance
CT & VT Testing
Injection Testing
Emergency Trip Test
Protection Testing / Settings
HV Metering CT & VT Test Certificate
Inuslation Resistance
Polarity Checks
Injection Testing
Metering Wiring Checks
Substation Earth Resistance Certificate
Target Earth Reading
Actual Earth Reading
As-laid (PDF, CAD, Visio, Any Scaled Format)
Main outside plot is connected to linkbox/transformer
Service Route if not on the Service Card
Locational dimensions on live cables and linkbox
HV As-laid Drawing (PDF, CAD, Visio, Any Scaled Format)
HV Cable Test Certificate
Pressure Test
Sheath Test
Continuity Testing
Small Power and Lighting Testing
Insulation Resistance
Continuity
Voltage
ELI
Circuit Rating

## Water Networks
Water Completion Data Requirements
Connect and vest mains
For the testing of the new mains: Please notify us at least 5 days in advance before conducting pressure and bacteriological tests.
Valid pass results must be sent to us within 1 calendar day of receipt.
CRMC Process
Submit request for Request for Permission to Work
Permission for mains connection will be given within 7 calendar days
Connection should be carried out on the agreed date and confirmed to us within 1 calendar day from the connection being made and Within 5 days of the connection being made, your Completed Work form should be submitted to us
Please also supply the below:
Completed Work Form
Pressure Test Certificates
Sample Test Certificates
Completed Vesting Certificate
Notification of plots for connection (copy of the certificate is included within the Adoption Agreement)
As-laid